## Sheet1
| Zone | Point | Point Name | Point Ref | Read/Write | Multistate Variable Occupancy status Modes (read/write)
Level | 00 Foyer Shared Workspace | Space temperature | Level 00 Foyer Shared Workspace Space temperature | AV1 | R | Unoccupied – Frost protection active – No comfort heating/cooling or Co2 control.
Level | 00 Foyer Shared Workspace | Space Co2 (if available for that room) | Level 00 Foyer Shared Workspace Space Co2 | AV2 | R | Standby – Heating and Cooling to 3°C either side of space temperature setpoint, Co2 control to setpoint.
Level | 00 Foyer Shared Workspace | Space Temperature Setpoint | Level 00 Foyer Shared Workspace Space Temperature Setpoint | AV3 | R/W | Occupied – Heating and Cooling to 1°C either side of space temperature setpoint, Co2 control to setpoint
Level | 00 Foyer Shared Workspace | Occupancy Status | Level 00 Foyer Shared Workspace Occupancy Status | MSV4 | R/W | CO2 is in PPM
Level | 00 Registrar Waiting Area | Space temperature | Level 00 Registrar Waiting Area Space temperature | AV4 | R | Temperature is in °C
Level | 00 Registrar Waiting Area | Space Co2 (if available for that room) | Level 00 Registrar Waiting Area Space Co2 | AV5 | R | CO2 reading is with 0 decimal point
Level | 00 Registrar Waiting Area | Space Temperature Setpoint | Level 00 Registrar Waiting Area Space Temperature Setpoint | AV6 | R/W | Temperature reading is with 1 decimal point
Level | 00 Registrar Waiting Area | Occupancy Status | Level 00 Registrar Waiting Area Occupancy Status | MSV7 | R/W | Temperature Setpoint is in 0.1 increments
Level | 00 Divisible Committee | Space temperature | Level 00 Divisible Committee Room 1 Space temperature | AV8 | R | Temperature setpoint range from 20°C to 24°C
Level | 00 Divisible Committee | Space Co2 (if available for that room) | Level 00 Divisible Committee Room 1 Space Co2 | AV9 | R
Level | 00 Divisible Committee | Space Temperature Setpoint | Level 00 Divisible Committee Room 1 Space Temperature Setpoint | AV10 | R/W
Level | 00 Divisible Committee | Occupancy Status | Level 00 Divisible Committee Room 1 Occupancy Status | MSV11 | R/W
|  |  | Level 00 Divisible Committee Room 2 Space temperature | AV12 | R
Level 00 Divisible Committee Room 1 Space temperature |  | R | Level 00 Divisible Committee Room 2 Space Co2 | AV13 | R
Level 00 Divisible Committee Room 1 Space Co2 (if available for that room) |  | R | Level 00 Divisible Committee Room 2 Space Temperature Setpoint | AV14 | R/W
Level 00 Divisible Committee Room 1 Space Temperature Setpoint |  | R/W | Level 00 Divisible Committee Room 2 Occupancy Status | MSV15 | R/W
Level 00 Divisible Committee Room 1 Occupancy Status |  | R/W | Level 00 Divisible Committee Room 3 Space temperature | AV16 | R
|  |  | Level 00 Divisible Committee Room 3 Space Co2 | AV17 | R | IP: | 10.192.32.80
Level | 00 Courtyard Rm | Space temperature | Level 00 Divisible Committee Room 3 Space Temperature Setpoint | AV18 | R/W | Gateway: | 10.192.32.1
Level | 00 Courtyard Rm | Space Co2 (if available for that room) | Level 00 Divisible Committee Room 3 Occupancy Status | MSV19 | R/W | Subnet Mask: | 255.255.255.128
Level | 00 Courtyard Rm | Space Temperature Setpoint | Level 00 Divisible Committee Room 4 Space temperature | AV20 | R
Level | 00 Courtyard Rm | Occupancy Status | Level 00 Divisible Committee Room 4 Space Co2 | AV21 | R
Level | 00 Courtyard Rm | Space temperature | Level 00 Divisible Committee Room 4 Space Temperature Setpoint | AV22 | R/W
Level | 00 Courtyard Rm | Space Co2 (if available for that room) | Level 00 Divisible Committee Room 4 Occupancy Status | MSV23 | R/W
Level | 00 Small Hall | Space temperature | Level 00 Courtyard Room 1 Space temperature | AV24 | R
Level | 00 Small Hall | Space Co2 (if available for that room) | Level 00 Courtyard Room 1 Space Co2 (if available for that room) | AV25 | R
Level | 00 Small Hall | Space Temperature Setpoint | Level 00 Courtyard Room 1 Space Temperature Setpoint | AV26 | R/W
Level | 00 Small Hall | Occupancy Status | Level 00 Courtyard Room 1 Occupancy Status | MSV27 | R/W
Level | 01 Assembly Hall | Space temperature | Level 00 Courtyard Room 2 Space temperature | AV28 | R
Level | 01 Assembly Hall | Space Co2 (if available for that room) | Level 00 Courtyard Room 2 Space Co2 (if available for that room) | AV29 | R
Level | 01 Assembly Hall | Space Temperature Setpoint | Level 00 Courtyard Room 2 Space Temperature Setpoint | AV30 | R/W
Level | 01 Assembly Hall | Occupancy Status | Level 00 Courtyard Room 2 Occupancy Status | MSV31 | R/W
Level | 01 Nigel Playfair Room | Space temperature | Level 00 Small Hall Space temperature | AV32 | R
Level | 01 Nigel Playfair Room | Space Co2 (if available for that room) | Level 00 Small Hall Space Co2 | AV33 | R
Level | 01 Nigel Playfair Room | Space Temperature Setpoint | Level 00 Small Hall Space Temperature Setpoint | AV34 | R/W
Level | 01 Nigel Playfair Room | Occupancy Status | Level 00 Small Hall Occupancy Status | MSV35 | R/W
Level | 01 Marble Gallery | Space temperature | Level 01 Assembly Hall Space temperature | AV36 | R
Level | 01 Marble Gallery | Space Co2 (if available for that room) | Level 01 Assembly Hall Space Co2 | AV37 | R
Level | 01 Marble Gallery | Space Temperature Setpoint | Level 01 Assembly Hall Space Temperature Setpoint | AV38 | R/W
Level | 01 Marble Gallery | Occupancy Status | Level 01 Assembly Hall Occupancy Status | MSV39 | R/W
Level | 01 Courtyard Rm Divisible | Space temperature | Level 01 Nigel Playfair Room Space temperature | AV40 | R
Level | 01 Courtyard Rm Divisible | Space Co2 (if available for that room) | Level 01 Nigel Playfair Room Space Co2 | AV41 | R
Level | 01 Courtyard Rm Divisible | Space Temperature Setpoint | Level 01 Nigel Playfair Room Space Temperature Setpoint | AV42 | R/W
Level | 01 Courtyard Rm Divisible | Occupancy Status | Level 01 Nigel Playfair Room Occupancy Status | MSV43 | R/W
Level | 02 Riverside Room | Space temperature | Level 01 Marble Gallery Space temperature | AV44 | R
Level | 02 Riverside Room | Space Temperature Setpoint | Level 01 Marble Gallery Space Temperature Setpoint | AV46 | R/W
Level | 02 Riverside Room | Occupancy Status | Level 01 Marble Gallery Occupancy Status | MSV47 | R/W
Level | 02 Courtyard Room Divisible | Space temperature | Level 01 Courtyard Room 3 Divisible Space temperature | AV48 | R
Level | 02 Courtyard Room Divisible | Space Co2 (if available for that room) | Level 01 Courtyard Room 3 Divisible Space Co2 | AV49 | R
Level | 02 Courtyard Room Divisible | Space Temperature Setpoint | Level 01 Courtyard Room 3 Divisible Space Temperature Setpoint | AV50 | R/W
Level | 02 Courtyard Room Divisible | Occupancy Status | Level 01 Courtyard Room 3 Divisible Occupancy Status | MSV51 | R/W
|  |  | Level 01 Courtyard Room 4 Divisible Space temperature | AV52 | R
Level | 02 Council Chamber and Public Viewing Gallery | Space temperature | Level 01 Courtyard Room 4 Divisible Space Co2 | AV53 | R
Level | 02 Council Chamber and Public Viewing Gallery | Space Co2 (if available for that room) | Level 01 Courtyard Room 4 Divisible Space Temperature Setpoint | AV54 | R/W
Level | 02 Council Chamber and Public Viewing Gallery | Space Temperature Setpoint | Level 01 Courtyard Room 4 Divisible Occupancy Status | MSV55 | R/W
Level | 02 Council Chamber and Public Viewing Gallery | Occupancy Status | Level 01 Courtyard Room 5 Divisible Space temperature | AV56 | R
Level | 03 Opposition Rooms | Space temperature | Level 01 Courtyard Room 5 Divisible Space Co2 | AV57 | R
Level | 03 Opposition Rooms | Space Co2 (if available for that room) | Level 01 Courtyard Room 5 Divisible Space Temperature Setpoint | AV58 | R/W
Level | 03 Opposition Rooms | Space Temperature Setpoint | Level 01 Courtyard Room 5 Divisible Occupancy Status | MSV59 | R/W
Level | 05 Meeting Room Small | Space temperature | Level 02 Riverside Room Space temperature | AV60 | R
Level | 05 Meeting Room Small | Space Co2 (if available for that room) | Level 02 Riverside Room Space Co2 | AV61 | R
Level | 05 Meeting Room Small | Space Temperature Setpoint | Level 02 Riverside Room Space Temperature Setpoint | AV62 | R/W
Level | 05 Meeting Room Small | Occupancy Status | Level 02 Riverside Room Occupancy Status | MSV63 | R/W
Level | 05 Meeting Room Large | Space temperature | Level 02 Courtyard Room 6 Divisible Space temperature | AV64 | R
Level | 05 Meeting Room Large | Space Co2 (if available for that room) | Level 02 Courtyard Room 6 Divisible Space Co2 | AV65 | R
Level | 05 Meeting Room Large | Space Temperature Setpoint | Level 02 Courtyard Room 6 Divisible Space Temperature Setpoint | AV66 | R/W
Level | 05 Meeting Room Large | Occupancy Status | Level 02 Courtyard Room 6 Divisible Occupancy Status | MSV67 | R/W
|  |  | Level 02 Courtyard Room 7 Divisible Space temperature | AV68 | R
Level | 05 Members Leaders Office | Space temperature | Level 02 Courtyard Room 7 Divisible Space Co2 | AV69 | R
Level | 05 Members Leaders Office | Space Co2 (if available for that room) | Level 02 Courtyard Room 7 Divisible Space Temperature Setpoint | AV70 | R/W
Level | 05 Members Leaders Office | Space Temperature Setpoint | Level 02 Courtyard Room 7 Divisible Occupancy Status | MSV71 | R/W
Level | 05 Members Leaders Office | Occupancy Status | Level 02 Courtyard Room 8 Divisible Space temperature | AV72 | R
Level | 05 Members Chief Executive Office | Space temperature | Level 02 Courtyard Room 8 Divisible Space Co2 | AV73 | R
Level | 05 Members Chief Executive Office | Space Co2 (if available for that room) | Level 02 Courtyard Room 8 Divisible Space Temperature Setpoint | AV74 | R/W
Level | 05 Members Chief Executive Office | Space Temperature Setpoint | Level 02 Courtyard Room 8 Divisible Occupancy Status | MSV75 | R/W
Level | 05 Member's Office and Cabinet Room | Space temperature | Level 02 Council Chamber and Public Viewing Gallery Space temperature | AV76 | R
Level | 05 Member's Office and Cabinet Room | Space Co2 (if available for that room) | Level 02 Council Chamber and Public Viewing Gallery Space Co2 | AV77 | R
Level | 05 Member's Office and Cabinet Room | Space Temperature Setpoint | Level 02 Council Chamber and Public Viewing Gallery Space Temperature Setpoint | AV78 | R/W
Level | 05 Member's Office and Cabinet Room | Occupancy Status | Level 02 Council Chamber and Public Viewing Gallery Occupancy Status | MSV79 | R/W
Level | 05 Member's Meeting Room 01 | Space temperature | Level 03 Opposition Room Space temperature | AV80 | R
Level | 05 Member's Meeting Room 01 | Space Co2 (if available for that room) | Level 03 Opposition Room Space Co2 | AV81 | R
Level | 05 Member's Meeting Room 01 | Space Temperature Setpoint | Level 03 Opposition Rooms Space Temperature Setpoint | AV82 | R/W
Level | 05 Member's Meeting Room 01 | Occupancy Status | Level 03 Opposition Rooms Occupancy Status | MSV83 | R/W
|  |  | Level 05 Meeting Room 01 Space temperature | AV84 | R
|  |  | Level 05 Meeting Room 01 Space Co2 | AV85 | R
|  |  | Level 05 Meeting Room 01 Space Temperature Setpoint | AV86 | R/W
|  |  | Level 05 Meeting Room 01 Occupancy Status | MSV87 | R/W
|  |  | Level 05 Meeting Room 02 Space temperature | AV88 | R
|  |  | Level 05 Meeting Room 02 Space Co2 | AV89 | R
|  |  | Level 05 Meeting Room 02 Space Temperature Setpoint | AV90 | R/W
|  |  | Level 05 Meeting Room 02 Occupancy Status | MSV91 | R/W
|  |  | Level 05 Members Leaders Office Space temperature | AV92 | R
|  |  | Level 05 Members Leaders Office Space Co2 | AV93 | R
|  |  | Level 05 Members Leaders Office Space Temperature Setpoint | AV94 | R/W
|  |  | Level 05 Members Leaders Office Occupancy Status | MSV95 | R/W
|  |  | Level 05 Members Chief Executive Office Space temperature | AV96 | R
|  |  | Level 05 Members Chief Executive Office Space Co2 | AV97 | R
|  |  | Level 05 Members Chief Executive Office Space Temperature Setpoint | AV98 | R/W
|  |  | Level 05 Members Chief Executive Office Occupancy Status | MSV99 | R/W
|  |  | Level 05 Member's Office and Cabinet Room Space temperature | AV100 | R
|  |  | Level 05 Member's Office and Cabinet Room Space Co2 | AV101 | R
|  |  | Level 05 Member's Office and Cabinet Room Space Temperature Setpoint | AV102 | R/W
|  |  | Level 05 Member's Office and Cabinet Room Occupancy Status | MSV103 | R/W
|  |  | Level 05 Member's Meeting Room 01 Space temperature | AV104 | R
|  |  | Level 05 Member's Meeting Room 01 Space Co2 (if available for that room) | AV105 | R
|  |  | Level 05 Member's Meeting Room 01 Space Temperature Setpoint | AV106 | R/W
|  |  | Level 05 Member's Meeting Room 01 Occupancy Status | MSV107 | R/W