## Sheet1 Cable Schedule
Cable Schedule | Hammersmith Town Hall
Name | Type | From Location | To Location | Drawing | Devices | Ballasts/Drivers | Cable | Description
AR/DA001/U1 | DALI | GF/LCP/01 | Self Contained WC's, BOH unknown area | WKSR-SPM-TH-OO_DR-Y-0180 | 3 | 50 | 1.5mm/2 Core | DA001
AR/DA002/U2 | DALI | GF/LCP/01 | Self Contained WC's, BOH unknown area | WKSR-SPM-TH-OO_DR-Y-0180 | 4 | 58 | 1.5mm/2 Core | DA002
|  |  | Entrance XZ fittings | WKSR-SPM-TH-02-DR-Y-0500 |  | 4 | 1.5mm/2 Core
AR/DA003U3 | DALI | GF/LCP/01 | Registrar Office, Corridor, Acc WC | WKSR-SPM-TH-OO_DR-Y-0180 | 6 | 48 | 1.5mm/2 Core | DA003
AR/DA004/U4 | DALI | GF/LCP/01 | Courtyard | WKSR-SPM-TH-OO_DR-Y-0180 | 4 | 25 | 1.5mm/2 Core | DA004
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0170 |  | 34
AR/DA005/U5 | DALI | GF/LCP/01 | Registrar Reception | WKSR-SPM-TH-OO_DR-Y-0180 | 5 | 52 | 1.5mm/2 Core | DA005
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0170 |  | 3
AR/DA006/U6 | DALI | GF/LCP/01 | Registrar Office, Bridal Suite | WKSR-SPM-TH-OO_DR-Y-0180 | 7 | 52 | 1.5mm/2 Core | DA006
AR/DA007/U7 | DALI | GF/LCP/01 | Self Contained WC's, Staff Kitchetter | WKSR-SPM-TH-OO_DR-Y-0180 | 0 | 47 | 1.5mm/2 Core | DA007
AR/DA008/U8 | DALI | GF/LCP/01 | Multifaith Rooms | WKSR-SPM-TH-OO_DR-Y-0180 | 3 | 42 | 1.5mm/2 Core | DA008
|  |  | Entrance XZ fittings | WKSR-SPM-TH-02-DR-Y-0500 |  | 4 | 1.5mm/2 Core
AR/DA009/U9 | DALI | GF/LCP/01 | Consultation Rooms | WKSR-SPM-TH-OO_DR-Y-0180 | 1 | 24 | 1.5mm/2 Core | DA009
|  | GF/LCP/01 | External Lvl1 XP, XM fittings | WKSR-SPM-TH-02-DR-Y-0501 |  | 11 | 1.5mm/2 Core
AR/DA010/U10 | DALI | GF/LCP/02 | Corridor, Build Room, IT Help Space | WKSR-SPM-TH-OO_DR-Y-0180 | 3 | 52 | 1.5mm/2 Core | DA010
AR/DA011/U11 | DALI | GF/LCP/02 | BOH, WC's, General Circulation | WKSR-SPM-TH-OO_DR-Y-0180 | 4 | 52 | 1.5mm/2 Core | DA011
AR/DA012/U12 | DALI | GF/LCP/02 | Small Hall, Plant Rooms | WKSR-SPM-TH-OO_DR-Y-0180 | 3 | 47 | 1.5mm/2 Core | DA012
AR/DA013/U13 | DALI | GF/LCP/02 | Courtyard Room, General Circ | WKSR-SPM-TH-OO_DR-Y-0180 | 6 | 47 | 1.5mm/2 Core | DA013
AR/DA014/U14 | DALI | GF/LCP/02 | Committee Rooms, General Circ | WKSR-SPM-TH-OO_DR-Y-0180 | 7 | 53 | 1.5mm/2 Core | DA014
AR/DA015/U15 | DALI | GF/LCP/02 | Committee Rooms, Kitchen | WKSR-SPM-TH-OO_DR-Y-0180 | 6 | 62 | 1.5mm/2 Core | DA015
AR/DA016/U16 | DALI | GF/LCP/02 | Shared Workspace, Staff Toilets | WKSR-SPM-TH-OO_DR-Y-0180 | 9 | 55 | 1.5mm/2 Core | DA016
AR/DA017/U17 | DALI | GF/LCP/02 | Shared Workspace, Changing Space | WKSR-SPM-TH-OO_DR-Y-0180 | 6 | 61 | 1.5mm/2 Core | DA017
AR/DA018/U18 | DALI | GF/LCP/02 | Shared Workspace | WKSR-SPM-TH-OO_DR-Y-0180 | 6 | 56 | 1.5mm/2 Core | DA018
AR/DA019/U19 | DALI | GF/LCP/02 | Toilets, Shared Workspace | WKSR-SPM-TH-OO_DR-Y-0180 | 8 | 62 | 1.5mm/2 Core | DA019
AR/DA020/U20 | DALI | GF/LCP/02 | Stairs 5&6? | WKSR-SPM-TH-OO_DR-Y-0180 | 3 | 8 | 1.5mm/2 Core | DA020
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0170 |  | 12 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-01-DR-Y-0171 |  | 16 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-02-DR-Y-0172 |  | 4 | 1.5mm/2 Core
|  |  | External XQ & XZ fittings | WKSR-SPM-TH-02-DR-Y-0500 |  | 15 | 1.5mm/2 Core
AR/DA021/U21 | DALI | GF/LCP/02 | Stairs 3&4? | WKSR-SPM-TH-OO_DR-Y-0180 | 4 | 8 | 1.5mm/2 Core | DA021
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0170 |  | 12 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-01-DR-Y-0171 |  | 16 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-02-DR-Y-0172 |  | 16 | 1.5mm/2 Core
|  |  | External XH Fittings | WKSR-SPM-TH-02-DR-Y-0500 |  | 2 | 1.5mm/2 Core
Name | Type | From Location | To Location | Drawing | Devices | Ballasts/Drivers | Cable | Description
AR/DA022/U22 | DALI | GF/LCP/01 | Stairs 1&2? | WKSR-SPM-TH-OO_DR-Y-0180 | 4 | 6 | 1.5mm/2 Core | DA022
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0170 |  | 12 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-01-DR-Y-0171 |  | 16 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-02-DR-Y-0172 |  | 16 | 1.5mm/2 Core
|  |  | External XH Fittings | WKSR-SPM-TH-02-DR-Y-0500 |  | 2 | 1.5mm/2 Core
AR/DY/101 | Dynet Spur | GF/LCP/01 | Registar PDTS | WKSR-SPM-TH-OO_DR-Y-0170 | 2 |  | CAT5e | AR/DY/101
AR/DY/102 | Dynet Spur | GF/LCP/01 | Consultation Rooms, Bridal Suite | WKSR-SPM-TH-OO_DR-Y-0170 | 8 |  | CAT5e | AR/DY/102
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0180 | 25 |  | CAT5e
AR/DY/103 | Dynet Link | GF/LCP/01 | GF/LCP/02 | WKSR-SPM-TH-OO_DR-Y-0170 | 0 |  | CAT5e | AR/DY/103
AR/DY/104 | Dynet Spur | GF/LCP/02 | Committee Rooms | WKSR-SPM-TH-OO_DR-Y-0170 | 4 |  | CAT5e | AR/DY/104
|  |  |  | WKSR-SPM-TH-OO_DR-Y-0180 | 17 |  | CAT5e
AR/DY/105 | Dynet Spur | GF/LCP/02 | Small Hall PDTS | WKSR-SPM-TH-OO_DR-Y-0170 | 1 |  | CAT5e | AR/DY/105
AR/DY/106 | Dynet Spur | GF/LCP/01 | Self Contained WC's | WKSR-SPM-TH-OO_DR-Y-0170 | 11 |  | CAT5e | AR/DY/106
AR/DY/107 | Dynet Spur | GF/LCP/02 | Shared Workspace PDTS | WKSR-SPM-TH-OO_DR-Y-0170 | 1 |  | CAT5e | AR/DY/107
AR/DY/108 | Dynet Spur | GF/LCP/02 | WC's, Help Room, IT Build | WKSR-SPM-TH-OO_DR-Y-0180 | 13 |  | CAT5e | AR/DY/108
AR/DY/109 | Dynet Spur | GF/LCP/02 | Ladies WC's | WKSR-SPM-TH-OO_DR-Y-0180 | 11 |  | CAT5e | AR/DY/109
AR/DMX/901 | DMX - Rx | GF/LCP/01 DMX Rx | Registrars Waiting Area MXLR Socket | MXLR 5 Pin DMX Input location TBC |  |  | CAT5e | AR/DMX/901
AR/DMX/902 | DMX - Rx | GF/LCP/02 DMX Rx | Small Hall MXLR Socket | MXLR 5 Pin DMX Input location TBC |  |  | CAT5e | AR/DMX/902
AR/DMX/903 | DMX - Rx | Courtyard GF level MXLR Socket | 4F/LCP/11 DMX Rx | MXLR 5 Pin DMX Input location TBC |  |  | CAT5e | AR/DMX/903
Internal Cabinet link | DMX - Tx | 1F/LCP/05/PharosLPC1 (RAIL FLIP) | RDM Splitter 01 | WKSR-SPM-TH-XX-DR-Y-0400 |  |  | CAT5e
AR/DA101/U23 | DALI | 1F/LCP/03 | Open Plan Office Space | WKSR-SPM-TH-01-DR-Y-0181 | 8 | 61 | 1.5mm/2 Core | DA101
AR/DA102/U24 | DALI | 1F/LCP/03 | General Circulation and H&F Workspace | WKSR-SPM-TH-01-DR-Y-0181 | 9 | 50 | 1.5mm/2 Core | DA102
AR/DA103/U25 | DALI | 1F/LCP/03 | Registrar Waiting Area | WKSR-SPM-TH-01-DR-Y-0181 |  | 40 | 1.5mm/2 Core | DA103
AR/DA104/U26 | DALI | 1F/LCP/03 | Self Contained WC's Registrar Waiting Area | WKSR-SPM-TH-01-DR-Y-0181 |  | 59 | 1.5mm/2 Core | DA104
AR/DA105/U27 | DALI | 1F/LCP/03 | General Circulation and H&F Workspace | WKSR-SPM-TH-01-DR-Y-0181 | 5 | 58 | 1.5mm/2 Core | DA105
AR/DA106/U28 | DALI | 1F/LCP/03 | General Circulation and Union Rooms | WKSR-SPM-TH-01-DR-Y-0181 | 10 | 58 | 1.5mm/2 Core | DA106
AR/DA107/U29 | DALI | 1F/LCP/03 | Self Contained WC's and General Circulation | WKSR-SPM-TH-01-DR-Y-0181 | 5 | 58 | 1.5mm/2 Core | DA107
AR/DA108/U30 | DALI | 1F/LCP/04 | General Circulation and H&F Workspace | WKSR-SPM-TH-01-DR-Y-0181 | 8 | 61 | 1.5mm/2 Core | DA108
AR/DA109/U31 | DALI | 1F/LCP/04 | Courtyard Rooms | WKSR-SPM-TH-01-DR-Y-0181 | 5 | 59 | 1.5mm/2 Core | DA109
AR/DA110/U32 | DALI | 1F/LCP/04 | Nigel Playfair | WKSR-SPM-TH-01-DR-Y-0181 | 8 | 53 | 1.5mm/2 Core | DA110
AR/DA111/U33 | DALI | 1F/LCP/04 | Marble Gallery | WKSR-SPM-TH-01-DR-Y-0181 | 9 | 59 | 1.5mm/2 Core | DA111
AR/DA112/U34 | DALI | 1F/LCP/04 | BOH Stairs Assembly Hall | WKSR-SPM-TH-01-DR-Y-0181 | 2 | 25 | 1.5mm/2 Core | DA112
|  |  |  | WKSR-SPM-TH-02-DR-Y-0172 |  | 2 | 1.5mm/2 Core
|  |  |  | WKSR-SPM-TH-02-DR-Y-0182 |  | 3 | 1.5mm/2 Core
|  |  | Assembley Hall DF fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 25 | 1.5mm/2 Core
AR/DA113/U79 | DALI | 1F/LCP/04 | External XA< XL Fittings Lvl1 | WKSR-SPM-TH-02-DR-Y-0501 |  | 35 | 1.5mm/2 Core | DA113
AH/DA114/U80 | DALI | 1F/LCP/05/PharosLPC1 | Assembly Hall DP & DF fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 57 | 1.5mm/2 Core | DA114
AR/DMX/101 |  | 1F/LCP/05/PharosLPC1 RDM Split Port 1 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/101
AR/DMX/102 |  | 1F/LCP/05/PharosLPC1 RDM Split 2 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/102
AR/DMX/103 |  | 1F/LCP/05/PharosLPC1 RDM Split 3 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/103
AR/DMX/104 |  | 1F/LCP/05/PharosLPC1 RDM Split 4 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/104
AR/DMX/105 |  | 1F/LCP/05/PharosLPC1 RDM Split 5 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/105
AR/DMX/106 |  | 1F/LCP/05/PharosLPC1 RDM Split 6 | Assembly Hall CA fittings | WKSR-SPM-TH-XX-DR-Y-0400 |  | 22 | CAT5e | AR/DMX/106
AR/DY/110 | Dynet Spur | 1F/LCP/03 | General Circulation, Plant Rooms and WC's | WKSR-SPM-TH-01-DR-Y-0181 | 21 |  | CAT5e | AR/DY/110
Name | Type | From Location | To Location | Drawing | Devices | Ballasts/Drivers | Cable | Description
|  |  | Union Rooms | WKSR-SPM-TH-01-DR-Y-0171 | 2
AR/DY/111 | Dynet Link | 1F/LCP/03 | 1F/LCP/04 | WKSR-SPM-TH-01-DR-Y-0171 | 0 |  | CAT5e | AR/DY/111
AR/DY/112 | Dynet Spur | 1F/LCP/04 | Nigel Playfair | WKSR-SPM-TH-01-DR-Y-0171 | 2 |  | CAT5e | AR/DY/112
|  |  |  | WKSR-SPM-TH-01-DR-Y-0181 | 3
AR/DY/113 | Dynet Spur | 1F/LCP/04 | Courtyard Rooms | WKSR-SPM-TH-01-DR-Y-0171 | 2 |  | CAT5e | AR/DY/113
|  |  | Plant and Courtyard Rooms | WKSR-SPM-TH-01-DR-Y-0181 | 16
AR/DY/114 | Dynet Link | 1F/LCP/04 | 1F/LCP/05/PharosLPC1 | WKSR-SPM-TH-01-DR-Y-0171 | 1 |  | CAT5e | AR/DY/114
AR/DY/115 | Dynet Spur | 1F/LCP/05/PharosLPC1 | Marble Gallery | WKSR-SPM-TH-01-DR-Y-0171 | 1 |  | CAT5e | AR/DY/115
AR/DY/116 | Dynet Spur | 1F/LCP/03 | General Circulation, Plant Rooms and WC's | WKSR-SPM-TH-01-DR-Y-0181 | 11 |  | CAT5e | AR/DY/116
AR/DMX/911 | DMX-Rx | 1F/LCP/04 | Nigel Playfair MXLR Wall Plate Socket | WKSR-SPM-TH-01-DR-Y-0171 |  |  |  | AR/DMX/911
AR/DMX/912 | DMX-Rx | 1F/LCP/04 | Marble Gallery MXLR Wall Plate Socket | WKSR-SPM-TH-01-DR-Y-0171 |  |  |  | AR/DMX/912
AR/DMX/913 | DMX-Rx | 1F/LCP/05/PharosLPC1 | Assembley Hall Rail Flip DMX input A from MXLR Socket | WKSR-SPM-TH-01-DR-Y-0171 |  |  |  | AR/DMX/913
AR/DA201/U35 | DALI | 2F/LCP/07 | H&F Workspace | WKSR-SPM-TH-02-DR-Y-0182 | 8 | 58 | 1.5mm/2 Core | DA201
AR/DA202/U36 | DALI | 2F/LCP/07 | General Circulation | WKSR-SPM-TH-02-DR-Y-0182 | 8 | 42 | 1.5mm/2 Core | DA202
AR/DA203/U37 | DALI | 2F/LCP/07 | Self Contained WC's, Riverside Room< H&F Workspace | WKSR-SPM-TH-02-DR-Y-0182 | 4 | 55 | 1.5mm/2 Core | DA203
AR/DA204/U38 | DALI | 2F/LCP/07 | Mayors Office & Parlour | WKSR-SPM-TH-02-DR-Y-0182 | 11 | 50 | 1.5mm/2 Core | DA204 | Over Max Dev
AR/DA205/U39 | DALI | 2F/LCP/07 | Council Chamber | WKSR-SPM-TH-02-DR-Y-0182 |  | 31 | 1.5mm/2 Core | DA205
|  |  |  | WKSR-SPM-TH-02-DR-Y-0172 |  | 30
AR/DA206/U40 | DALI | 2F/LCP/07 | Council Chamber Task Lighting | WKSR-SPM-TH-02-DR-Y-0172 |  | 60 | 1.5mm/2 Core | DA206
AR/DA207/U41 | DALI | 2F/LCP/07 | Self Contained WC's | WKSR-SPM-TH-02-DR-Y-0182 |  | 39 | 1.5mm/2 Core | DA207
|  |  | Mayors Foyer Standard Lamps Allowance | WKSR-SPM-TH-02-DR-Y-0172 |  | 15
AR/DA208/U42 | DALI | 2F/LCP/06 | H&F Workspace | WKSR-SPM-TH-02-DR-Y-0182 | 8 | 61 | 1.5mm/2 Core | DA208
AR/DA209/U43 | DALI | 2F/LCP/06 | General Circulation and Lift Lobby | WKSR-SPM-TH-02-DR-Y-0182 | 10 | 43 | 1.5mm/2 Core | DA209
|  |  | Handrails | WKSR-SPM-TH-02-DR-Y-0172 |  | 8
AR/DA210/U44 | DALI | 2F/LCP/06 | H&F Workspace & Plant | WKSR-SPM-TH-02-DR-Y-0182 | 3 | 61 | 1.5mm/2 Core | DA210
AR/DA211/U45 | DALI | 2F/LCP/06 | General Circulation and Plant | WKSR-SPM-TH-02-DR-Y-0182 | 7 | 31 | 1.5mm/2 Core | DA211
AR/DA212/U46 | DALI | 2F/LCP/06 | H&F Workspace, BOH Stairs & Plant | WKSR-SPM-TH-02-DR-Y-0182 | 4 | 51 | 1.5mm/2 Core | DA212
AR/DA213/U47 | DALI | 2F/LCP/06 | Marble Gallery, AYA and AYB fittings | WKSR-SPM-TH-02-DR-Y-0182 |  | 44 | 1.5mm/2 Core | DA213
|  |  | External Lvl2 XA Fittings | WKSR-SPM-TH-02-DR-Y-0502 |  | 15 | 1.5mm/2 Core
AR/SWL/57 | Mains | 2F/LCP/07 (Live wire only thru DDRC420FR) | Mayors Foyer Standard Lamps Allowance | WKSR-SPM-TH-02-DR-Y-0172 |  | 3 | 240Vac | SWL1
AR/SWL/58 | Mains | 2F/LCP/07 (Live wire only thru DDRC420FR) | Mayors Foyer Standard Lamps Allowance | WKSR-SPM-TH-02-DR-Y-0172 |  | 4 | 240Vac | SWL2
AR/SWL/59 | Mains | 2F/LCP/07 (Live wire only thru DDRC420FR) | Mayors Foyer Standard Lamps Allowance | WKSR-SPM-TH-02-DR-Y-0172 |  | 3 | 240Vac | SWL3
AR/SWL/58 | Mains | 2F/LCP/07 (Live wire only thru DDRC420FR) | Mayors Foyer Standard Lamps Allowance | WKSR-SPM-TH-02-DR-Y-0172 |  | 4 | 240Vac | SWL4
AR/DY/217 | Dynet Link | 2F/LCP/06 | 1F/LCP/07 | WKSR-SPM-TH-02-DR-Y-0172 | 0 |  | CAT5e | AR/DY/217
AR/DY/218 | Dynet Spur | 2F/LCP/06 | Mayors Office & Parlour | WKSR-SPM-TH-02-DR-Y-0172 | 3 |  | CAT5e | AR/DY/218
AR/DY/219 | Dynet Spur | 2F/LCP/06 | Council Chamber | WKSR-SPM-TH-02-DR-Y-0172 | 14 |  | CAT5e | AR/DY/219
AR/DY/220 | Dynet Spur | 2F/LCP/07 | H&F Workspace & Marble Gallery | WKSR-SPM-TH-02-DR-Y-0172 | 12 |  | CAT5e | AR/DY/220
AR/DY/221 | Dynet Spur | 2F/LCP/07 | Courtyard Rooms | WKSR-SPM-TH-02-DR-Y-0172 | 15 |  | CAT5e | AR/DY/221
AR/DY/222 | Dynet Spur | 2F/LCP/06 | Toilet and Council Chamber Sensors. | WKSR-SPM-TH-03-DR-Y-0182 | 30 |  | CAT5e | AR/DY/222
AR/DA301/U48 | DALI | 3F/LCP/08 | H&F Workspace | WKSR-SPM-TH-03-DR-Y-0182 | 8 | 52 | 1.5mm/2 Core | DA301
AR/DA302/U49 | DALI | 3F/LCP/08 | WC's, General Circulation | WKSR-SPM-TH-03-DR-Y-0182 | 7 | 55 | 1.5mm/2 Core | DA302
AR/DA303/U50 | DALI | 3F/LCP/08 | Skylight, Mayors Foyer, External Walkway | WKSR-SPM-TH-03-DR-Y-0182 | 7 | 40 | 1.5mm/2 Core | DA303
Name | Type | From Location | To Location | Drawing | Devices | Ballasts/Drivers | Cable | Description
|  |  | Stairs | 11375-LA-173 |  | 8 | 1.5mm/2 Core
|  |  | External XL Fixtures Lvl3 | WKSR-SPm-TH-03-DR-Y-0503 |  | 6 | 1.5mm/2 Core
AR/DA304/U51 | DALI | 3F/LCP/08 | Skylight, Mayors Foyer, External Walkway | WKSR-SPM-TH-03-DR-Y-0182 | 5 | 42 | 1.5mm/2 Core | DA304
|  |  | Stairs | 11375-LA-173 |  | 8 | 1.5mm/2 Core
|  |  | External XL Fixtures Lvl3 | WKSR-SPm-TH-03-DR-Y-0503 |  | 6 | 1.5mm/2 Core
AR/DA305/U52 | DALI | 3F/LCP/08 | WC's, General Circulation | WKSR-SPM-TH-03-DR-Y-0182 |  | 58 | 1.5mm/2 Core | DA305
|  |  | Public Galleries Handrails | 11375-LA-173 |  | 4 | 1.5mm/2 Core
AR/DA306/U53 | DALI | 3F/LCP/08 | General Circulation, Lift Lobby | WKSR-SPM-TH-03-DR-Y-0182 | 7 | 34 | 1.5mm/2 Core | DA306
|  |  | Courtyard Lift Lobby Handrails | 11375-LA-173 |  | 6 | 1.5mm/2 Core
AR/DA307/U54 | DALI | 3F/LCP/09 | H&F Workspace | WKSR-SPM-TH-03-DR-Y-0182 | 8 | 53 | 1.5mm/2 Core | DA307
AR/DA308/U55 | DALI | 3F/LCP/09 | Opposition Offices & Stores | WKSR-SPM-TH-03-DR-Y-0182 |  | 54 | 1.5mm/2 Core | DA308
|  |  | Stairs | 11375-LA-173 |  | 8 | 1.5mm/2 Core
AR/DA309/U56 | DALI | 3F/LCP/09 | General Circulation, Assembley Hall BOH Stage Lighting | WKSR-SPM-TH-03-DR-Y-0182 | 9 | 47 | 1.5mm/2 Core | DA309
|  |  | Stairs | 11375-LA-173 |  | 8 | 1.5mm/2 Core
AR/DA310/U57 | DALI | 3F/LCP/09 | Assembley Hall, Stores, General Circulation | WKSR-SPM-TH-03-DR-Y-0182 | 10 | 42 | 1.5mm/2 Core | DA310
AR/DA311/U58 | DALI | 3F/LCP/09 | Stores, Plant, General Circculation | WKSR-SPM-TH-03-DR-Y-0182 | 2 | 47 | 1.5mm/2 Core | DA311
AR/DY/321 | Dynet Spur | 3F/LCP/08 | WC's, General Circulation, | WKSR-SPM-TH-03-DR-Y-0182 | 28 |  | CAT5e | AR/DY/321
AR/DY/322 |  |  | Council Chamber, Mayors Foyer button stations | 11375-LA-173 | 2 |  |  | AR/DY/322
AR/DY/323 | Dynet Link | 3F/LCP/08 | 3F/LCP/09 | WKSR-SPM-TH-03-DR-Y-0182 |  |  | CAT5e | AR/DY/323
AR/DMX/931 | DMX - Tx | 3F/LCP/08 | Mayors Foyer CW Fittings | WKSR-SPM-TH-03-DR-Y-0182 |  | 14 | CAT5e | AR/DMX/931
AR/DY/324 | Dynet Spur | 3F/LCP/09 | Opposition Offices & Stores | WKSR-SPM-TH-03-DR-Y-0182 | 12 |  | CAT5e | AR/DY/324
|  |  | Opposition Offices button stations | 11375-LA-173 | 2 |  | CAT5e
AR/DY/325 | Dynet Spur | 3F/LCP/09 | Stores, Plant, General Circculation | WKSR-SPM-TH-03-DR-Y-0182 | 6 |  | CAT5e | AR/DY/325
AR/DA401/U59 | DALI | 4F/LCP/11 | Courtyard General Circulation | WKSR-SPM-TH-04-DR-Y-0184 |  | 18 | 1.5mm/2 Core | DA401
|  |  | Courtyard Handrail | WKSR-SPM-TH-04-DR-Y-0174 |  | 20 | 1.5mm/2 Core
AR/DA402/U60 | DALI | 4F/LCP/11 | Courtyard DG Fittings and EM's | WKSR-SPM-TH-04-DR-Y-0184 |  | 57 | 1.5mm/2 Core | DA402
AR/DA403/U61 | DALI | 4F/LCP/11 | Courtyard and Roof | WKSR-SPM-TH-04-DR-Y-0184 |  | 45 | 1.5mm/2 Core | DA403
|  |  | External XL Fixtures Lvl4 | WKSR-SPM-TH-04-DR-Y-0504 |  | 5 | 1.5mm/2 Core
AR/DA404/U62 | DALI | 4F/LCP/11 | Courtyard | WKSR-SPM-TH-04-DR-Y-0184 | 1 | 46 | 1.5mm/2 Core | DA404
|  |  | External XL Fixtures Lvl4 | WKSR-SPM-TH-04-DR-Y-0504 |  | 5 | 1.5mm/2 Core
AR/DA405/U63 | DALI | 4F/LCP/11 | WC's and General Circulation | WKSR-SPM-TH-04-DR-Y-0184 | 3 | 48 | 1.5mm/2 Core | DA405
AR/DA406/U64 | DALI | 4F/LCP/11 | Plant, Stairs and General Circulation | WKSR-SPM-TH-04-DR-Y-0184 | 4 | 34 | 1.5mm/2 Core | DA406
|  |  | External XL Fixtures Lvl4 | WKSR-SPM-TH-04-DR-Y-0504 |  | 5 | 1.5mm/2 Core
AR/DY/426 | Dynet Spur | 4F/LCP/11 | Courtyard | WKSR-SPM-TH-04-DR-Y-0184 | 22 |  | 1.5mm/2 Core | AR/DY/426
AR/DY/427 | Dynet Spur | 4F/LCP/11 | General Circulation | WKSR-SPM-TH-04-DR-Y-0184 |  |  |  | AR/DY/427
AR/DMX/941 | DMX-Tx | 5F/LCP/10/Storm1 port1 | BZ Row 1-4 East | WKSR-SPM-TH-04-DR-Y-0184 | 4 | 48 | CAT5e | AR/DMX/941
AR/DMX/942 | DMX-Tx | 5F/LCP/10/Storm1 port2 | BZ Row 5-14 East | WKSR-SPM-TH-04-DR-Y-0184 | 10 | 120 | CAT5e | AR/DMX/942
AR/DMX/943 | DMX-Tx | 5F/LCP/10/Storm1 port3 | BZ Row 15-24 East | WKSR-SPM-TH-04-DR-Y-0184 | 10 | 120 | CAT5e | AR/DMX/943
AR/DMX/944 | DMX-Tx | 5F/LCP/10/Storm1 port4 | BZ Row 25-30 East | WKSR-SPM-TH-04-DR-Y-0184 | 6 | 70 | CAT5e | AR/DMX/944
AR/DMX/945 | DMX-Tx | 5F/LCP/10/Storm1 port5 | BZ Row 1-4 West | WKSR-SPM-TH-04-DR-Y-0184 | 4 | 48 | CAT5e | AR/DMX/945
AR/DMX/946 | DMX-Tx | 5F/LCP/10/Storm1 port6 | BZ Row 5-14 West | WKSR-SPM-TH-04-DR-Y-0184 | 10 | 120 | CAT5e | AR/DMX/946
AR/DMX/947 | DMX-Tx | 5F/LCP/10/Storm1 port7 | BZ Row 15-24 West | WKSR-SPM-TH-04-DR-Y-0184 | 10 | 120 | CAT5e | AR/DMX/947
AR/DMX/948 | DMX-Tx | 5F/LCP/10/Storm1 port8 | BZ Row 25-30 West | WKSR-SPM-TH-04-DR-Y-0184 | 6 | 48 | CAT5e | AR/DMX/948
AR/DMX/949 | DMX-Tx | 5F/LCP/10/Storm1 port9 (RAIL FLIP) | 5F/LCP/10/ARLF/01 Input B |  |  |  | CAT5e | AR/DMX/949
AR/DMX/411 | DMX-Tx | 5F/LCP/10/ALRF/01 Output 1 | BN Profiles | WKSR-SPM-TH-04-DR-Y-0174 | 14 |  | CAT5e | AR/DMX/411
Name | Type | From Location | To Location | Drawing | Devices | Ballasts/Drivers | Cable | Description
AR/DMX/Link | DMX-Rx | 4F/LCP/11 NG03 Port 2 Output | 5F/LCP/10/ARLF/01 Input A | On schematic not on any dwg extension of AR/DMX/903 |  |  | CAT5e | AR/DMX/Link
AR/DY/528 | Dynet Spur | 5F/LCP/12 | Toilets and central UI's | WKSR-SPM-TH-05-DR-Y-0185 | 13 |  | CAT5e | AR/DY/528
AR/DY/529 |  |  | Offices and unknown areas | WKSR-SPM-TH-05-DR-Y-0175 | 4 |  | CAT5e | AR/DY/529
AR/DY/528 | Dynet Spur | 5F/LCP/12 | Toilets | WKSR-SPM-TH-05-DR-Y-0185 | 29 |  | CAT5e | AR/DY/528
AR/DY/529 |  |  | General Circulation | WKSR-SPM-TH-05-DR-Y-0175 | 4 |  | CAT5e | AR/DY/529
AR/DA501/U65 | DALI | 5F/LCP/12 | Courtyard and Lift Lobby | WKSR-SPM-TH-05-DR-Y-0185 | 3 | 30 | 1.5mm/2 Core | DA501
|  |  | Lift Loby Handrails | WKSR-SPM-TH-05-DR-Y-0175 |  | 4 | 1.5mm/2 Core
|  |  | Lift Lobby lvl6 | WKSR-SPM-TH-05-DR-Y-0186? |  | 10 | 1.5mm/2 Core
|  |  | Lift Lobby Handrail Lvl6 |  |  | 4 | 1.5mm/2 Core
| DALI |  | External XX Fixtures Lvl6 |  |  | 12 | 1.5mm/2 Core
AR/DA502/U66 | DALI | 5F/LCP/12 | Courtyard | WKSR-SPM-TH-05-DR-Y-0185 | 10 | 51 | 1.5mm/2 Core | DA502
AR/DA503/U67 | DALI | 5F/LCP/12 | General Circulation, Stores | WKSR-SPM-TH-05-DR-Y-0185 |  | 61 | 1.5mm/2 Core | DA503
AR/DA504/U68 | DALI | 5F/LCP/12 | Courtyard | WKSR-SPM-TH-05-DR-Y-0185 | 8 | 55 | 1.5mm/2 Core | DA504
AR/DA505/U69 | DALI | 5F/LCP/12 | General Circulation | WKSR-SPM-TH-05-DR-Y-0185 | 6 | 58 | 1.5mm/2 Core | DA505
AR/DA506/U70 | DALI | 5F/LCP/12 | General Circulation, Stores | WKSR-SPM-TH-05-DR-Y-0185 |  | 58 | 1.5mm/2 Core | DA506
AR/DA507/U71 | DALI | 5F/LCP/12 | WC, Stores, Plant | WKSR-SPM-TH-05-DR-Y-0185 |  | 57 | 1.5mm/2 Core | DA507
AR/DA508/U72 | DALI | 5F/LCP/12 | Office Spaces | WKSR-SPM-TH-05-DR-Y-0185 | 8 | 55 | 1.5mm/2 Core | DA508
AR/DA509/U73 | DALI | 5F/LCP/12 | Office Spaces | WKSR-SPM-TH-05-DR-Y-0185 | 4 | 59 | 1.5mm/2 Core | DA509
AR/DA510/U74 | DALI | 5F/LCP/12 | Office Spaces | WKSR-SPM-TH-05-DR-Y-0185 | 6 | 45 | 1.5mm/2 Core | DA510
AR/DA602/U75 | DALI | 5F/LCP/12 | 6f Unknown | WKSR-SPM-TH-05-DR-Y-0186? | 4 | 58 | 1.5mm/2 Core | DA602
AR/DA603/U76 | DALI | 5F/LCP/12 | 6f General Circulation, BOH Stairs | WKSR-SPM-TH-05-DR-Y-0186? | 5 | 41 | 1.5mm/2 Core | DA603
AR/DA604/U77 | DALI | 5F/LCP/12 | 6f Toilets | WKSR-SPM-TH-05-DR-Y-0186? |  | 27 | 1.5mm/2 Core | DA604
AR/DA605/U78 | DALI | 5F/LCP/12 | 6f BOH, WC's, General Circulation | WKSR-SPM-TH-05-DR-Y-0186? | 4 | 58 | 1.5mm/2 Core | DA605
AR/DY/630 | Dynet Spur | 5F/LCP/12 | Dynet devices 6f RCP | WKSR-SPM-TH-05-DR-Y-0185 | 8 |  | CAT5e | AR/DY/630
AR/DY/631 | Dynet Spur | 5F/LCP/12 | Dynet devices 6f RCP | WKSR-SPM-TH-05-DR-Y-0185 | 10 |  | CAT5e | AR/DY/631
AR/DMX/906 | DMX-Tx | 5F/LCP/10/Storm1 port10 | XK Fittings | WKSR-SPM-TH-05-DR-Y-0505 |  | 23 | CAT5e | AR/DMX/906
AR/DMX/907 | DMX-Tx | 5F/LCP/10/Storm1 port11 | XK Fittings | WKSR-SPM-TH-05-DR-Y-0505 |  | 23 | CAT5e | AR/DMX/907
AR/DMX/908 | DMX-Tx | 5F/LCP/10/Storm1 port12 | XK Fittings | WKSR-SPM-TH-05-DR-Y-0505 |  | 11 | CAT5e | AR/DMX/908
AR/DMX/909 | DMX-Tx | 5F/LCP/10/Storm1 port13 | XK Fittings | WKSR-SPM-TH-05-DR-Y-0505 |  | 11 | CAT5e | AR/DMX/909

## Sheet2 LAN Requirements
Cable Schedule | Hammersmith Town Hall
Name | Type | Description | Cabinet Location | Drawing | Actual Location | IP Address | Subnet | Gateway | DNS | VLAN | Internet Access
00F/HTH/GatewayP01 | PDEG | Primary Node for BMS | GF/LCP/01 | GF Indicative Mark Up | TBC | 10.10.10.1 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
00F/Courtyard/GatewayP02 | PDEG | Courtyard Area Control DALI control | GF/LCP/02 | GF Indicative Mark Up | TBC | 10.10.10.2 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
1F/AssembleyHall/GWP03 | PDEG | Assembley Hall DALI Control | 1F/LCP/03 | 1F Indicative Mark Up | TBC | 10.10.10.3 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
1F/NigelPlayfair/GWP04 | PDEG | Nigel Playfair DALI control | 1F/LCP/04 | 1F Indicative Mark Up | TBC | 10.10.10.4 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
1F/LCP/Pharos02 | Pharos | Pharos VLAN A Comms | 1F/LCP/05 | 1F Assembley Hall Indicative Mark UP | TBC | 10.10.10.20 | 255.255.255.0 | 10.10.10.254 | 8.8.8.8 | A | YES
2F/HTH/GatewayP05 | PDEG | Network Dynet Comms | 2F/LCP/06 | 2F Indicative Mark Up | TBC | 10.10.10.5 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
3F/HTH/GatewayP06 | PDEG | Network Dynet Comms | 3F/LCP/09 | 3F Indicative Mark Up | TBC | 10.10.10.6 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
4F/HTH/GatewayP07 | PDEG | Network Dynet Comms | 4F/LCP/11 | 4F Indicative Mark Up | TBC | 10.10.10.7 | 255.255.255.0 | 10.10.10.254 | NO | A | NO
5F/PharosLPCX MGMT | Pharos | Pharos VLAN A Comms | 5F/LCP/10 | 4F Indicative Mark Up | TBC | 10.10.10.21 | 255.255.255.0 | 10.10.10.254 | 8.8.8.8 | A | YES
5F/PharosLPCX Data | Pharos | Couryard DMX Control | 5F/LCP/10 | 4F Indicative Mark Up | TBC | TBC | 255.0.0.0 | TBC | NO | B | NO
5F/HTH/GatewayP08 | PDEG | Network Dynet Comms | 5F/LCP/12 | 5F Indicative Mark Up | TBC | 10.10.10.8 | 255.255.255.0 | 10.10.10.254 | NO | A | NO

## Sheet3 Area Preset Schedule
Area Schedule | Hammersmith Town Hall
Name | Access Point | Rm No. | Area Number | Rig Test | Day | Evening | Off | Gloomy Day | Night | Standby | Presentation | User Preset 1 | User Preset 2
Assembly Hall | Any |  | 202 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Marble Gallery | Any |  | 202: 203
Council Chamber | Any |  | 202: 206
Mayors Foyer | Any |  | 202: 207
Courtyard | Any |  | 202: 208
External Façade | Any |  | 202: 209
Committee Rm01 | DTK622-232 GF/LCP/01 | 0.03 | 202: 6
Committee Rm02 |  | 0.04 | 202: 7
Committee Rm03 |  | 0.05 | 202: 8
Committee Rm04 |  | 0.06 | 202: 9
Small Hall |  | 0.08 | 202: 11
Courtyard Rm01 |  | 0.11 | 202: 14
Courtyard Rm02 |  | 0.12 | 202: 15
Consultation Rm01 |  | 0.25 | 202: 26
Consultation Rm02 |  | 0.26 | 202: 27
Consultation Rm03 |  | 0.27 | 202: 28
Consultation Rm04 |  | 0.28 | 202: 29
Consultation Rm05 |  | 0.29 | 202: 30
Consultation Rm06 |  | 0.3 | 202: 31
Registrar Offices |  | 0.32 | 202: 32
Bridal Suite |  | 0.33 | 202: 33
Powder Rm |  | 0.34 | 202: 34
Courtyard Rm05 | DTK622-232 1F/LCP/04 | 1.04 | 202: 2
Courtyard Rm04 |  | 1.05 | 202: 3
Courtyard Rm03 |  | 1.06 | 202: 4
Open Plan Office Space |  | 1.08 | 202: 5
Nigel Playfair Rm |  | 1.09 | 202: 6
H&F Workspace |  | 1.14 | 202: 9
Union Rm01 |  | 1.15 | 202: 11
Union Rm02 |  | 1.16 | 202: 12
Registrar Waiting Area |  | 1.17 | 202: 13
H&F Workspace | DTK622-232 2F/LCP/06 | 2.02 | 202: 81
Courtyard Rm06 |  | 2.05 | 202: 82
Courtyard Rm07 |  | 2.06 | 202: 83
Courtyard Rm08 |  | 2.07 | 202: 84
H&F Office Space |  | 2.11 | 202: 87
Riverside Rm |  | 2.12 | 202: 88
Mayors Palour |  | 2.13 | 202: 89
Mayors Office |  | 2.14 | 202: 90
H&F Office Space |  | 2.15 | 202: 91
Opposition Office | DTK622-232 3F/LCP/09 | 3.04 | 202: 111
Opposition Meeting Rm |  | 3.05 | 202: 112
H&F Workspace |  | 3.07 | 202: 113
Public Gallerys |  | 3.11 | 202: 115
H&F Workspace |  | 3.14 | 202: 117
Skylight Lighting |  | 3.17 | 202: 118